SECTION 08 33 00

# ROLLING COUNTER FIRE DOORS WITH INTEGRAL FRAME

GENERAL NOTES TO SPECIFIER:

THIS SPECIFICATION SECTION HAS BEEN PREPARED TO ASSIST DESIGN PROFESSIONALS IN THE PREPARATION OF PROJECT OR OFFICE MASTER SPECIFICATIONS. IT FOLLOWS GUIDELINES ESTABLISHED BY THE CONSTRUCTION SPECIFICATIONS INSTITUTE, AND THEREFORE MAY BE USED WITH MOST MASTER SPECIFICATION SYSTEMS WITH MINOR EDITING.

EDIT CAREFULLY TO SUIT PROJECT REQUIREMENTS. MODIFY AS NECESSARY AND DELETE ITEMS THAT ARE NOT APPLICABLE. VERIFY THAT REFERENCED SECTION NUMBERS AND TITLES ARE CORRECT. (NUMBERS AND TITLES REFERENCED ARE BASED ON MASTERFORMAT(, 2004 EDITION).

THIS SECTION ASSUMES THE PROJECT MANUAL WILL CONTAIN COMPLETE DIVISION 1 DOCUMENTS INCLUDING SECTIONS 01 33 00 SUBMITTAL PROCEDURES, 01 62 00 PRODUCT OPTIONS, 01 25 13 PRODUCT SUBSTITUTION PROCEDURES, 01 66 00 PRODUCT STORAGE AND HANDLING REQUIREMENTS, 01 77 00 CLOSEOUT PROCEDURES, AND 01 78 00 CLOSEOUT SUBMITTALS. IF THE PROJECT MANUAL DOES NOT CONTAIN THESE SECTIONS, ADDITIONAL INFORMATION SHOULD BE INCLUDED UNDER THE APPROPRIATE ARTICLES.

THIS IS AN OPEN PROPRIETARY SPECIFICATION ALLOWING USERS THE OPTION OF APPROVING OTHER MANUFACTURERS WHICH COMPLY WITH THE CRITERIA SPECIFIED HEREIN.

NOTES TO THE SPECIFIER ARE CONTAINED IN BOXES AND SHOULD BE DELETED FROM FINAL COPY.

OPTIONAL ITEMS REQUIRING SELECTION BY THE SPECIFIER ARE ENCLOSED WITHIN BRACKETS, E.G.: [35] [40] [45]. IN CASES WHERE ONE OF THE OPTIONAL ITEMS IS A STANDARD FEATURE OF THE DOOR MODEL, IT IS LISTED IN THE FIRST POSITION. MAKE APPROPRIATE SELECTION AND DELETE OTHERS.

ITEMS REQUIRING ADDITIONAL INFORMATION ARE UNDERLINED, E.G.:  ____________.

OPTIONAL PARAGRAPHS ARE SEPARATED BY A REDLINED "OR," E.G.:

OR

PART 1 GENERAL

1.1	SUMMARY

A.	Section Includes:

1.	Manual push-up operated automatic closing rolling counter fire doors with integral frame [and countertop], built-in type.

OR

1.	Manual push-up operated automatic closing rolling counter fire doors with integral frame [and countertop], slip-in type.

B.	Related Sections:

1.	05 50 00 Metal Fabrications. Door opening jamb and head members.

2.	06 10 00 Rough Carpentry. Door opening jamb and head members.

3.	08 31 00 Access Doors and Panels. Access doors.

4.	08 70 00 Hardware. Padlocks. Masterkeyed cylinder.

5.	09 91 00 Painting. Field painting.

6.	Division 26. Electrical wiring and conduit for connection to alarm system.

C.	Products That May Be Supplied, But Are Not Installed Under This Section:

1.	Smoke/heat detectors.

2.	Annunciator.

INCLUDE APPROPRIATE LANGUAGE BELOW, INCLUDING A REFERENCE TO SECTION 01 23 00 ALTERNATES, IF ROLLING COUNTER FIRE DOORS WITH INTEGRAL FRAMES ARE INCLUDED IN ANY ALTERNATES, ADD SECTION 01 23 00 TO 1.1 B. DELETE IF NO ALTERNATES.

D.	Alternates:

1.2	SYSTEM DESCRIPTION

A.	Performance Requirements:

1.	Provide doors with Underwriters' Laboratories, Inc. label for the fire rating classification [1 1/2 hour] [1 hour] [3/4 hour].

1.3	SUBMITTALS

A.	Reference Section 01 33 00 Submittal Procedures; submit the following items:

1.	Product Data.

2.	Shop Drawings: Include special conditions not detailed in Product Data. Show interface with adjacent work.

3.	Quality Assurance/Control Submittals:

a.	Provide proof of manufacturer ISO 9001:2000 registration.

b.	Provide proof of manufacturer and installer qualifications - see 1.4 below.

c.	Provide manufacturer's installation instructions.

4.	Closeout Submittals:

a.	Operation and Maintenance Manual.

b.	Certificate stating that installed materials comply with this specification.

1.4	QUALITY ASSURANCE

A.	Qualifications:

1.	Manufacturer Qualifications: ISO 9001:2000 registered and a minimum five years experience in producing rolling counter fire doors with integral frames of the type specified.

2.	Installer Qualifications: Manufacturer's approval.

1.5	DELIVERY STORAGE AND HANDLING

A.	Reference Section 01 66 00 Product Storage and Handling Requirements.

B.	Follow manufacturer's instructions.

1.6	WARRANTY

A.	Standard Warranty: Two years from date of shipment against defects in material and workmanship.

B.	Maintenance: Submit for owner’s consideration and acceptance of a maintenance service agreement for installed products.

PART 2 PRODUCTS

2.1	MANUFACTURER

A.	Manufacturer: Clopay Building Products Co., 8585 Duke Blvd., Mason, OH 45040-3101. Telephone: (800) 282-2260. Underwriters Laboratories, Inc. (UL), ISO 9001:2000 Registered.

INSERT NAME, ADDRESS, AND PHONE NUMBERS OF LOCAL DISTRIBUTOR BELOW.

1.	Distributor:

B.	Model: CERC20

C.	Substitutions: Reference Section 01 25 13 Product Substitution Procedures.

2.2	MATERIALS

A.	Curtain:

1.	Slats: No. 1F, interlocked flat-faced slats, 1-1/2 inches (38 mm) high by 1/2 inch (13 mm) deep, 22 gauge ASTM A 653, Commercial Quality, galvanized steel with plain steel bottom bar and vinyl astragal.

OR

1.	Slats: No. 1F, interlocked flat-faced slats, 1-1/2 inches (38 mm) high by 1/2 inch (13 mm) deep, 22 gauge AISI type 304 series stainless steel with stainless steel bottom bar and vinyl astragal.

2.	Fabricate continuous interlocking slat sections with high strength galvanized steel endlocks riveted to slat ends per UL requirements.

3.	Slat Finish:

a.	GalvaNex( Coating System to include an ASTM A 653 galvanized base coating treated with dual process rinsing agents in preparation of a chemical bonding, light gray baked-on polyester base coat and a light gray baked-on polyester finish coat. The scientific organic material composition and chemical bonding process of GalvaNex( produces a superior finish against corrosion and abrasion. GalvaNex( components include a limited two year finish warranty.

OR

- GalvaNex( Coating System and phosphate treatment followed by baked-on polyester powder coat, [color as selected by Architect from manufacturer's standard color range, minimum 32 colors] [custom color as selected by Architect]; minimum 2.5 mils (0.065 mm) cured film thickness; ASTM D-3363 pencil hardness: H or better.

OR

a.	Stainless Steel: No. 4 finish.

4.	Bottom Bar Finish:

a.	Steel: Phosphate treatment followed by a light gray baked-on polyester powder coat; minimum 2.5 mils (0.065 mm) cured film thickness.

OR

a.	Steel: Phosphate treatment followed by baked-on polyester powder coat, [color as selected by Architect from manufacturer's standard color range, minimum 32 colors] [custom color as selected by Architect]; minimum 2.5 mils (0.065 mm) cured film thickness; ASTM D-3363 pencil hardness: H or better.

OR

a.	Steel: ASTM A 123, Grade 85 zinc coating, hot-dip galvanized.

OR

a.	Stainless Steel: No. 4 finish.

B.	Head and Jamb Frame: Integral welded with guide groove incorporated into jamb design. Build to fit _____” (_____ mm) wall thickness.

1.	Steel: 16 gauge formed shapes

OR

1.	Stainless Steel: 16 gauge AISI 300 series formed shapes.

2.	Finish:

a.	Steel: Light gray shop prime coat; minimum 0.6 mils (0.015 mm) cured film						thickness.

OR

a.	Stainless steel: No. 4 finish.

DELETE BELOW IF INTEGRAL STAINLESS STEEL COUNTERTOP IS NOT TO BE PROVIDED WITH ROLLING COUNTER FIRE DOOR WITH INTEGRAL FRAME.

C.	Countertop: Integral 14 gauge AISI 300 series stainless steel formed shape; No. 4 finish.

D.	Counterbalance Shaft Assembly:

1.	Barrel: Steel pipe capable of supporting curtain load with maximum deflection of 0.03 inches per foot (2.5 mm per meter) of width.

2.	Spring Balance: Oil-tempered, heat-treated steel helical torsion spring assembly designed for proper balance of door to ensure that maximum effort to operate will not exceed 25 lbs (110 N). Provide wheel for applying and adjusting spring torque.

E.	Brackets: Fabricate from reinforced [steel] [AISI 300 series stainless steel] plate with bearings at rotating support points to support counterbalance shaft assembly and form end closures for hood.

1.	Finish:

a.	Steel: Light gray shop prime coat; minimum 0.6 mils (0.015 mm) cured film thickness.

OR

a.	Stainless Steel: No. 4 finish.

F.	Hood [and Fascia]: [16 gauge steel] [16 gauge stainless steel] with reinforced top and bottom edges.

1.	Finish:

a.	Steel: Light gray shop prime coat; minimum 0.6 mils (0.015 mm) cured film						thickness.

OR

a.	Stainless Steel: No. 4 finish.

VERIFY BUILDING CODE REQUIREMENTS FOR SMOKE SEALS AND DELETE IF NOT REQUIRED. IF SMOKE SEALS ARE REQUIRED, CHECK CODE FOR SMOKE DETECTOR AND ALARM SYSTEM TIE-IN REQUIREMENTS.

G.	Smoke Seals:

1.	Bottom Bar: UL Tested PVC double bulb seal.

2.	Guides and Head: Replaceable, UL Listed, nylon pile smoke seals sealing against fascia side of curtain.

2.3	ACCESSORIES

MOST COMMON LOCKING METHODS ARE LISTED BELOW; CONSULT CLOPAY COMMERCIAL INFORMATION ASSISTANCE (800) 526-4301 OPTION #3 FOR OTHER OPTIONS.

A.	Locking: Padlockable slide bolt on coil side of bottom bar at each jamb extending into slots in guides.

OR

A.	Locking: Masterkeyable cylinder operable from [coil] [fascia] [both] side[s] of bottom bar.

PLASTIC LAMINATE COUNTERTOPS ARE AVAILABLE IN LIEU OF INTEGRAL STAINLESS STEEL COUNTERTOP. INCLUDE IF DESIRED AND DELETE 2.2-C. 12” (305 mm) MINIMUM COUNTERTOP DEPTH; 36” (914 mm) MAXIMUM COUNTERTOP DEPTH.

B.	Countertop: 1 ½ Hour UL Labeled, 1-5/8” (41 mm) thick, plastic laminate covered, size and configuration made for opening size and wall construction. Color as selected by Architect from standard range of Wilson Art or Formica plastic laminates.

C.	[Photoelectric Smoke/Heat Detector] [Ionization Smoke Detector]: UL listed.

FIRE EMERGENCY ANNUNCIATORS ARE AVAILABLE FOR USE WITH FIREGARD SERIES RELEASE DEVICES. HORN/STROBE AVAILABLE WITH ALL FIREGARD SERIES DEVICES; VOICE WARNING MODULE AVAILABLE WITH TYPE BV DEVICE ONLY. COORDINATE WITH SECTION 2.5-B, DELETE IF NOT DESIRED.

D.	Fire Emergency Annunciator: [Provide ADA compliant horn/strobe] [Provide Voice Warning Module] fire emergency annunciator to give advanced warning that the counter fire door is about to close. Warning signal to activate upon alarm signal.

2.4	FABRICATION

A.	Factory weld head, [and] jambs [and countertop] into a single unit, fully assembled, ready for installation.

2.5	OPERATION

A.	Manual Push-Up: Manual lift or pole with hook.

B.	Automatic Closing and Speed Governor Mechanism:

1.	Fusible Link with AR-D Release Device:

a.	Activation: [Central alarm system] [Local smoke and heat detectors] or power outage in excess of 10 seconds or melting of fusible link.

b.	Average Closing Speed: Not less than 6 inches (152 mm) nor more than 24 inches (610 mm) per second.

c.	Reset Procedure: Reset spring tension and mechanical dropouts; reset FireGard AR-D or replace fusible link.

OR

1.	Fusible Link with BB Release Device:

a.	Activation: [Central alarm system] [Local smoke and heat detectors] or power outage in excess of 72 hours or melting of fusible link.

b.	Average Closing Speed: Not less than 6 inches (152 mm) nor more than 24 inches (610 mm) per second.

c.	Reset Procedure: Reset spring tension and mechanical dropouts; reset FireGard BB or replace fusible link.

OR

1.	Fusible Link with DC Release Device:

a.	Activation: [Central alarm system] [Local smoke and heat detectors], DC alarm system power outage or melting of fusible link.

b.	Average Closing Speed: Not less than 6 inches (152 mm) nor more than 24 inches (610 mm) per second.

c.	Reset Procedure: Reset spring tension and mechanical dropouts; reset FireGard DC or replace fusible link.

OR

1.	Fusible Link:

a.	Activation: Melting of fusible link.

b.	Average Closing Speed: Not less than 6 inches (152 mm) nor more than 24 inches (610 mm) per second.

c.	Reset Procedure: Reset spring tension and mechanical dropouts; replace fusible link.

PART 3 EXECUTION

3.1	EXAMINATION

A.	Examine substrates upon which work will be installed and verify conditions are in accordance with approved shop drawings.

B.	Coordinate with responsible entity to perform corrective work on unsatisfactory substrates.

C.	Commencement of work by installer is acceptance of substrate.

3.2	INSTALLATION

A.	General: Install door unit and operating equipment with necessary hardware, anchors, inserts, hangers and supports.

B.	Comply with NFPA 80 and follow manufacturer's installation instructions.

3.3	ADJUSTING

A.	Following completion of installation, including related work by others, lubricate, test, and adjust doors for ease of operation, free from warp, twist, or distortion.

3.4	FIELD QUALITY CONTROL

A.	Site Test: Test doors for normal operation and automatic closing. Coordinate with authorities having jurisdiction to witness test and sign Drop Test Form.

3.5	CLEANING

A.	Clean surfaces soiled by work as recommended by manufacturer.

B.	Remove surplus materials and debris from the site.

3.6	DEMONSTRATION

A.	Demonstrate proper operation to Owner's Representative.

B.	Instruct Owner's Representative in maintenance procedures.

END OF SECTION